Health and Safety Services

Guidance on the maintenance of electrical equipment by

Schools / Administrative Directorates.

Introduction

- The Electricity at Work Regulations 1989 places a legal duty on the University to prevent injury to staff, students and visitors from its electrical systems. It is essential that electrical equipment is properly maintained so as to prevent danger. This document details the University’s approach to ensuring electrical equipment is safe and remains so.

Responsibilities

- The University Board of Governors has delegated responsibility for electrical safety as follows.

- It is the responsibility of the Director of Estates to ensure that (i) the fixed wiring of every University owned/ managed building and (ii) centrally provided equipment eg lifts, air conditioning units etc are inspected, tested and maintained on a regular basis by competent persons in accordance with the Electricity at Work Regulations and the IEE Code of Practice for In-Service Inspection & Testing of Electrical Equipment.  Appropriate records are to be kept.

- It is the responsibility of each Head of School or Head of Administrative Directorate (or equivalent) to have all their electrical equipment - fixed, transportable and portable – inspected, tested and maintained at regular intervals in accordance with the Electricity at Work Regulations and the IEE Code of Practice for In-Service Inspection & Testing of Electrical Equipment.

- New electrical equipment - should be inspected for condition before use.  This inspection should include the items listed in paragraphs 7 and 8 relevant to new equipment.  Any new equipment shall be subject to a full combined inspection and test within its first 12 months in service.  This is particularly important for equipment brought in from outside the UK.

- The frequency of inspection and testing will depend on the equipment, use, location etc.  The Head of School/ Directorate may need to make use of a competent person to advise him/her on the appropriate frequency of testing and on the tests to be performed.

- Testing and inspection must only be carried out by personnel who are competent in testing and inspection of the types of equipment submitted for testing.  Personnel who perform testing can be University employees or outside contractors who are members of a recognized electrical contracting association. The Directorate of Estates obtains tenders every three years for PAT testing for the administrative directorates and other faculties may choose to make use of this information. (See Appendix 1 for details)  Advice can be obtained from the Directorate’s Electrical Engineer.

- It is the responsibility of each Head of School/ Head of Administrative Directorate/Division to ensure that members of staff are familiar with the hazards of the electrical equipment they are to use and understand basic safety precautions.

- It is the responsibility of every member of staff, student and visitor to take care of their own safety and that of others.  They must not use or allow to be used equipment which is obviously faulty.  They must check each piece of electrical equipment before it is used. [See paragraph 7.]

Maintaining (including testing of) Portable and Transportable Electrical Equipment

- Maintenance - employers have a responsibility under Regulation 4(2) of the Electricity at Work Regulations 1989 to maintain portable and transportable electrical equipment so as to prevent danger. The Health & Safety Executive (HSE) sees maintenance comprising :

a)	A visual inspection of appliances. This comprises a daily check by the user for hand held and hand operated items AND a formal check at set intervals by a nominated person for all appliances which operate at mains voltage.

b)	Electrical testing of earth continuity/insulation integrity (using a portable appliance tester for example) of all earthed appliances and certain double insulated items by a competent person at set intervals.

c)	Repair and replacement consequent to a) and b) above.

- Visual inspection by users - all users must look critically at the electrical equipment they use from time to time. This needs to be daily in the case of hand held and hand operated appliances to check that the equipment is in sound condition (remember to unplug and switch off first!!).

They must check for :-

i)	damage, e.g. cuts, abrasion (apart from light scuffing) to the cable covering;

ii)	damage to plug, e.g. the casing is cracked or the pins are bent;

iii)	non-standard joints including taped joints in the cable;

iv)	the outer covering (sheath) of the cable not being gripped where it enters the plug or the equipment.  (Look to see if the coloured insulation of the internal wires is showing);

v)	equipment that has been used in conditions where it is not suitable, e.g. a wet or dusty workplace;

- damage to the outer cover of the equipment or obvious loose parts or screws;

vii)	signs of overheating (burn marks or staining).

The checks also apply to extension leads, associated plugs and sockets.

Any faults must be reported to the line manager and the equipment taken out of use immediately and labelled as faulty (and why).  It must not be used again until repaired.

Note: Equipment which exhibits intermittent faults must be taken out of service and not used again until thoroughly checked out by a competent person and the source of the fault identified and rectified.

- Formal Visual Inspection by a Nominated Person - these must take place at set intervals, dependent on risk.  They will include the checks in paragraph 11 above plus removal of the plug cover to check:

i)	a  fuse is being used (eg it is a proper fuse not a piece of wire, a nail etc) ;

ii)	the cord grip is holding the outer part (sheath) of the cable tightly;

iii)	the wires, including the earth where fitted, are attached to the correct terminals;

iv)	no bare wire is visible other than at the terminals;

v)	the terminal screws are tight;

vi)	there is no sign of internal damage, overheating or entry of liquid, dust or dirt.

These checks also apply to extension leads and their plugs, but not to moulded plugs where only the fuse can be checked.

A suggested frequency for formal visual inspections is given in the table below.

- The HSE states that the formal visual inspection can be carried out by a sensible member of staff (called a 'nominated person' in this document), provided they have enough knowledge and training.  They need to be able to avoid danger to themselves and others.  They should have basic electrical knowledge together with common sense eg switch off and unplug equipment first.  They must also know when the limit of knowledge and experience has been reached.

- Testing Of Portable Electrical Equipment - for earth/insulation integrity e.g. using a portable appliance tester, will be required in addition to a visual inspection (it is called 'combined inspection and testing' by the HSE):

a)	whenever there is a reason to suppose the equipment may be defective (but this cannot be confirmed by visual inspection);

b)	after any repair, modification or similar work;

c)	at regular intervals (these intervals will be determined by carrying out a risk assessment which will consider the equipment, the manner of use, frequency of use and the environment).  [See paragraph 12.]

- A visual inspection must also be carried out in conjunction with the electrical testing.  It should include the points referred to in paragraph 11 plus checking of the correct fusing and the suitability of the equipment for its environment.

- Combined inspection and testing should be carried out by someone with a wider degree of competence than that required for visual inspection alone. This is because the results of the tests may require interpretation and appropriate electrical knowledge.  This work can, however, often be carried out by an existing employee.  Such persons may need training.  The Staff Training and Development Unit regularly run one-day courses to train staff to carry out this basic testing. Alternatively, Schools may use external electrical contractors (see Responsibilities above and the Appendix for contractor details).

- Further advice on using external contractors for PAT is available from the electrical engineers in Estates Professional Services.

- As the table below shows, it is NOT a legal requirement to test portable equipment annually.  The inspection and test intervals should be determined on the basis of risk.  However, it is sometimes convenient to arrange for annual testing of all appliances, if the testers are on site to look at some of them.

- Recording – strictly speaking, this is not required by law but the HSE state "you may find it helpful if you have a lot of electrical equipment to keep track of and also to help you review your maintenance procedures.  Experience of faults found will determine whether inspection intervals can be lengthened and whether and how often there should be a combined inspection and test".

- University Schools are recommended to record both formal visual and electrical checks except where the number of items to be maintained is low.  Suggested model forms appear at the end of this document. The use of these forms is not compulsory as many areas store this information electronically, which is also acceptable. It does serve, however, to indicate the fields to record and will be presented on the STDU training courses.  The evidence of records would help in any legal case following an accident involving electrical appliances.

- Where records are kept, items of equipment need to be easily identifiable e.g. bear unique numbers, so the test results can be linked directly to the items. Keeping separate records of faults found will also assist in directing the test program to vulnerable areas (see I.E.E. guidance cited in the Reference section).

- Frequency Of Inspection – the initial frequency for inspection/testing suggested by the Health and Safety Executive follows. This frequency can be shortened or lengthened in the light of practical experience i.e. number of faults which appear.

- If Heads of Schools have difficulty in deciding how often to inspect/test they should seek advice from competent persons from inside or outside the University. The Estates Directorate are one such source of help and advice.

Initial Frequency of Checks Suggested by the HSE

A.	Higher Risk Environments

The HSE suggest that in industry formal visual inspections need to be carried out every 3 months and combined inspection and electrical tests every 6-12 months.

Heads of Schools in 'practical areas' will need to bear this figure in mind when drawing up a schedule for testing in their school.  It is quite likely that different inspection intervals will be required for laboratories, offices, and other areas.  Experience will decide (hence keeping of records is helpful).

B.	Offices and other low-risk environments

## Equipment/environment	User checks	Formal visual		Combined

inspection		inspection &

testing

Battery-operated:	No	No	No

(less than 20 volts)

Extra low voltage:	No	No	No

(less than 50 volts AC)

eg telephone equipment,

low voltage desk lights

Information technology:	No	Yes, 2-4	No if double

eg desktop computers,	years	insulated, otherwise

VDU screens		up to 5 years

Double insulated equipment:	No	Yes, 2-4	No

NOT hand-held.  Moved	years

occasionally, eg fans, table

lamps, slide projectors

Double insulated equipment:	Yes	Yes, 6 months	No

HAND-HELD eg some floor	   - 1 year

cleaners

__________________________________________________________________________

Earthed equipment (Class 1)	Yes	Yes, 6 months	Yes, 1-2 years

eg electric  kettles, some 		- 1 year

floor cleaners

(a) Cables (leads) and plugs	Yes	Yes, 6 months	Yes, 1-5 Years

connected to the above	- 4 years

equipment and

(b)  Extension leads	depending on the 	depending on the (used at mains voltage) 	type of equipment	type of equipment

Maintaining Fixed Electrical Equipment

- The requirement under Regulation 4(2) Electricity at Work Regulations to maintain (and test) portable and transportable electrical equipment also applies to fixed items of electrical equipment owned by a School/Directorate. ‘Fixed items’ covers those electrical items wired directly into the mains without use of a plug.  The range of this type of equipment in the University is vast, ranging from a wall mounted electric water heater, large laboratory centrifuges, lathes in workshops to liquid nitrogen plants.

The maintenance requirement on fixed appliances mirrors that of portable ones - visual check, earth continuity and insulation integrity tests.

- HS(R)25 entitled 'Memorandum of guidance on the Electricity at Work Regulations 1989' produced by the HSE (see References) states that advice on inspection and testing of fixed installations can be found in British Standards, and IEE Wiring Regulations and it lists a number of them.

- Departments who have fixed appliances need to contact the Directorate of Estates Electrical Engineer prior to carrying out this work (whether they intend to do this work themselves or engage others to do it for them).

- The frequency of the electrical tests is likely to be of the order of 5 years, but again will need to be decided on a case by case basis by carrying out a risk assessment.

Advice for staff and students in the use of electrical equipment

- The Electricity at Work Regulations 1989 place a duty on the University to train users to appreciate the dangers which could arise from incorrect/improper use of electrical equipment.  The following '10 helpful hints' should help staff and students to avoid the main dangers presented by the use of electricity in the University namely shock, fire and burns. This Guidance could be incorporated into a School’s Safety Policy.

- The Health and Safety at Work Act requires people at work to be responsible for their own safety (and the safety of others) and this includes not using equipment which is obviously defective.  Every member of staff and every student or visitor must regularly check the electrical equipment they intend to use, (or intend to give to others to use) to ensure no defects are apparent. 'Regularly' will vary from appliance to appliance. Every time it is used for hand held items such as electric drills, weekly for electric kettles, six monthly for VDUs, annually for 'fridges etc. [See paragraph 12 on testing frequency]. All new equipment brought into the School Directorate must be checked and entered onto the equipment inventory before first use.

- Users etc must visually check for:-

a)	damage to the cable [cuts, squashing of cable]

b)	exposed wires [usually visible due to cuts etc in the cable]

c)	broken/cracked plugs

d)	damage to the cable grip where the cable meets the plug.  [The internal yellow/blue/brown 'wires' etc must not be visible where the flex enters the plug]

e)	signs of overheating [brown stains around the 'pins' of the plug]

f)	broken or loose fitting parts of the equipment and its cover.

g)	a 'test sticker' to indicate the equipment has been formally inspected. The equipment must not be used if the test date is no longer valid.

- In addition employees (and others) must:

- Not use any equipment which is defective or damaged.  Label the item 'out of order' (sign and date the note) to prevent others using it, and lock the item away.  Report the defect immediately to the Supervisor / Manager.

- Make no attempt to repair or make alterations to equipment or remove permanently fixed covers from equipment (unless authorized to do so).

- Always switch off and unplug equipment before cleaning and fitting new parts (where authorized to do so).

- Always remove plugs from sockets by holding the plug and not by pulling on the cord, nor move equipment by pulling on the cord.

- Always check that cables are not squashed under furniture, or touching warm radiators, or trailing through liquids.

- Avoid food and drink coming into contact with electrical equipment, such as VDU keyboards.

- Seek the permission of the Head of School before bringing personal items of electrical equipment into the University for use. Any such personal items of equipment must be safe and be included in the regular departmental testing scheme.

- Route trailing cables away from walkways where passers-by may trip or drag the equipment off the desk/worktop.  Rubber coving for floor mounted cables is a sensible course of action.

- Avoid socket adapters which enable more than one plug to be plugged in to a single socket.  Trailing socket boards are a better but not fool proof alternative.

- Stop and ask your supervisor if you don't know if something is 'right' (or suspect something is 'wrong')!

- Electrical Equipment Test Record Sheet and Faulty Electrical Equipment Test Record Sheet  can be used to record testing data.

References

The Electricity at Work Regulations 1989 Regulations are supported by numerous Health and Safety Executive publications. Some of these publications are free and can be seen on the Health & Safety Executive's web sites e.g.

HSE - PUBLICATIONS: Free Leaflets

HS(R) 25 Memorandum of guidance on the Electricity at Work Regulations 1989  ISBN 978 0 7176 6228 9

INDG 231 ‘Electrical Safety and You’.

Safety in electrical testing: Servicing and repair of audio, TV and computer equipment (Engineering Information Sheet 36)

More detailed HSE publications, for which there is a charge, may be found by accessing: HSE Books - Home  and running a search for 'electrical safety'

These priced documents can be bought on-line or are available from the Stationery Office, Princess St, Manchester. It is also possible to view them via the John Rylands University Library electronic database Info4Education (OHSIS) – Athens password required.

Guidance on various electrical topics is also available from the Institution of Engineering and Technology , P.O. Box 96, Stevenage, Herts., SG1 2SD (see also their Web site at http://www.theiet.org/ )

(1) Code of Practice for In-Service Inspection and Testing of Electrical Equipment. ISBN 0 85296 776 4.

(2) 16th Edition I.E.E. Wiring Regulations (BS 7671:2000)

Appendix

The contractor appointed for the Registrar & Secretary's Directorates is

Integral,

Unit 1,

Rex Works,

Harvest Lane,

Sheffield

S3 8EB.

The main contact is:

Tom Durose (Contracts Manager)

Tel        0114 263 4277

Mob      0780 268 6266

E-mail   tom.durose@integral.co.uk

http://www.integral.co.uk/index.php

They are also available to work elsewhere in the University.   Contact via the electrical engineers in Estates Professional Services,

| Document control box |  |
| --- | --- |
| Policy / Procedure / Guidance title: | Guidance on the Maintenance of Electrical Equipment by Schools / Directorates |
| Implementation date: | June 2008 |
| Version: | v 2.0 |
| Supersedes: | University Code of Practice and Guidance on Maintenance of Electrical Equipment by Schools / Central Administration |
| Previous review dates: | 26 March 2006 |
| Next review date: | Upon significant change |
| Related documents: |  |
| Related Policies: | Health & Safety Policy |
| Related Procedures and Guidance: | A-Z of documents on specific health & safety topics, at http://www.campus.manchester.ac.uk/healthandsafety/CoPs&Guidance.htm |
| Policy owner: | Dr M J Taylor, University Safety Advisor |
| Lead contact: | Dr M J Taylor, University Safety Advisor |
| Further information: |  |